## Instructions
ODOUR AND CORROSION RISK ASSESSMENT TOOL - INSTRUCTIONS
Document Number: | SAW-TS-0854-SUP
Revision Number: | Revision 01
Revision Date: | 2025-09-29
Introduction
The Odour and Corrosion (O&C) Risk Assessment Tool is a support tool for the semi-quantitative assessment of O&C risks for sewerage network infrastructure. The key objective of the Tool is to guide the selection of appropriate design features and mitigations, based on risk levels, to effectively manage O&C risks for new sewerage assets when connecting to SA Water's existing network.
The Tool is to be used in conjunction with the SA Water Odour Technical Standard (insert link to location). The overarching O&C risk assessment framework and background to the Tool are set out in this Standard.
The key users of the Tool are expected to be designers of new sewerage assets, e.g. for the development of residential areas, who wish to connect new assets to SA Water's existing sewerage infrastructure. It is expected that these users will be SA Water and external parties.
The Tool is focussed on addressing risks for proposed new residential and commercial developments, including new residential estates and residential infill projects. Assessment of O&C risks for broad systems, e.g. including trunk sewers for transport of sewage to treatment facilities, is addressed separately by SA Water as part of their master planning processes.
OBJECTIVES: For new sewerage projects, objectives for hydrogen sulphide (H2S) gas space concentrations and dissolved sulphide concentrations in sewage within sewerage networks are set to target the ongoing effective management of O&C risks and are used to inform infrastructure designs as well as performance assessments following implementation. For SA Water networks, these targets are:
- H2S gas concentration in sewer gas space: |  | 10 ppm (on a peak or 90th percentile basis)
- Dissolved sulphide concentration in sewage: |  | 0.5 mg/L
Overview of the O&C Risk Assessment Tool
The O&C Risk Assessment Tool is an integral component of the overall O&C risk assessment approach. The process constitutes three assessment 'gates' where specific information is collected and used to determine if further and more detailed assessment is required. The description of these assessment gates is set out below, with an overview shown in Figure A, refer tab "Assessment Overview (Fig A)".
Level 1
Level 1 assessment involves basic screening testing to identify any risk 'triggers', as identified in tab "Level 1 Screening". If no risk triggers are identified, there is no need to progress to a Level 2 assessment. In such cases prima facie, no special conditions related to management of C&O issues are required for application approval The outcomes from the Level 1 assessment are to be documented and submitted to SA Water for review and approval.
Note: Where there are no risk triggers identified, this will inherently mean that each of the minimum design requirements, as set out in the Odour Technical Standard, have been met for the proposed new infrastructure.
If risk triggers are identified, the user is to progress to a Level 2 assessment.
Level 2
The Level 2 assessment is the focus of this Tool and requires the collection and input of hydraulic and design data for the proposed new infrastructure in to a Calculator. It is expected that this information will mostly be outputs from hydraulic design calculations, however, as for the Level 1 Assessment, there will be inputs which the Designer will need to obtain from SA Water by submission of a RFI. These items are as indicated in the Tool Level 2 AssessmentThe Calculator applies a risk score based on the input value for each of the risk criteria and determines an overall score and a subsequent O&C risk ranking. The risk rank output of the Tool informs the appropriate design features to be applied and/or minimum level of mitigations to be implemented, with guidance for the appropriate mitigations provided in the SA Water Odour Technical Standard document.
Level 2 Input information Calculator requirements are provided at tab "Level 2 Inputs". For some input parameters, higher weightings are applied where the parameters are deemed to have greater influence on overall potential risk. These parameters are:
- Hydraulic residence time (HRT) - for each of initial flow and ultimate development sewage flow scenarios.
- Number of sewage pumping stations (SPS) upstream of the proposed development infrastructure, i.e. extent of daisy-chaining.
- Distance from vent/release point to closest sensitive receptor
- Materials of construction
- Pressure main (PM) discharge maintenance hole configuration
The summary of the Calculator results for a Level 2 assessment is provided at tab "Level 2 Results". This provides a gauge indicating the overall risk rating consistent with SA Water's risk categories as summarised below.
A summary of the risk rankings and subsequent actions are shown below. Where risk levels are 'Medium', further work and design revisions are required to reduce risk levels to either 'Very Low' or 'Low'. Where the risk level is 'High', further detailed investigation is required in conjunction with SA Water, including selection of appropriate mitigations and/or design changes, to reduce the risk level to an acceptable level by SA Water. Only sewerage infrastructure for new developments with 'Very Low' or 'Low' risk rankings will be acceptable to SA Water.
A summary of the risk rankings and subsequent actions is shown below.
Very low risk | No further assessment. Ensure all minimum mandatory design rules are satisfied and provide Summary report to SA Water.
Low risk | Assess opportunities to reduce risks by adjustments to design (or mitigations) and update design accordingly. This is to be demonstrated and documented in the reporting.
Re-assess residual risk level, confirm appropriate mitigations. See the SA Water Odour Technical Standard for appropriate mitigations to address risks for different assets.
Medium risk | Apply appropriate O&C mitigations, as set out in the Odour Technical Standard.
Re-assess residual risk level, confirm appropriate mitigations. See the SA Water Odour Technical Standard for appropriate mitigations to address risks for different assets.
High risk | Further detailed assessment as set out in Level 3 (below) is required.
Level 3
Level 3 assessments are to be undertaken where the risk ranking output from the Level 2 O&C Risk Tool calculator indicates a 'High' risk. These applications typically occur where there are extended sewage residence times, turbulence and/or contribution of significant flows to downstream assets. They can also involve more complex issues such as atypical sewage quality, e.g. due to significant seawater ingress, trade waste impacts.
The Level 3 assessment is a detailed assessment and should be undertaken on a more systemic basis (or at least linked with system based planning). It could involve one or more of the following activities:
- Monitoring of gas and liquid data in upstream and downstream networks, i.e. up and downstream of proposed new connections.
- Septicity assessment using sulphide modelling. There are various tools for sulphide modelling ranging from basic spreadsheet calculations through to detailed modelling using proprietary software/tools such as WATS (Wastewater Aerobic / Anaerobic Transformations in Sewers). This could include assessment of extended regions downstream of the proposed new development infrastructure to consider broader impacts.
- Ventilation modelling, e.g. using WATS or AFT Arrow.
- Identification of appropriate mitigation facilities, e.g. chemical dosing at SPS (or gravity mains), forced ventilation of sewers with extracted gas treatment, renewal/rehabilitation of sewers with non-corrodible materials.
- Optioneering, including financial and whole of life assessments, of identified mitigation options.
- Air dispersion modelling to assess impacts of different mitigation options.
TASKS: How to Use the O&C Risk Assessment Tool
Key tasks to be undertaken by the User are outlined in the Steps below:
Step 1: Define the boundary of assessment
Define the boundary of the development infrastructure assets to be assessed. The assets within the scope of work will include the new development infrastructure assets and a minimum of 300 metres of the existing sewer downstream of the proposed connection point, and (as appropriate) 100 metres upstream of the proposed connection point.
Step 2: Collate design information
Collate the project design basis information, including hydraulic operating scenarios to be assessed, proposed development infrastructure design (pipe lengths, sizes, locations, etc.).
Identify and apply the minimum design rules, as set out in the Odour Technical Standard, e.g. for PM discharge maintenance hole (MH) designs, minimum and maximum sewer pipe velocities.
Step 3: Carry out Level 1 Screening checks
Use the 'Level 1 Screening' tab in this spreadsheet to answer basic project design queries. A 'YES' response to any of the questions indicates the User is to proceed to a Level 2 assessment, as directed in the steps below.
If all responses to the Screening questions are 'NO', document the project design data and outcomes of the Screening checks for SA Water review.
Step 4: Insert the input data for Level 2 assessment
Use the 'Inputs' tab in this spreadsheet to input required information to the Calculator.
Where no data are available, type 'N/A' or select 'N/A' from the drop down list where available.
Inputs are required as both user-determined values, e.g. hydraulic retention time (HRT) hours, and selection from drop-down cells.
Step 5: Review Calculator results
Check the risk assessment calculator 'Results' tab. This tab provides an overall risk ranking for the project, and shows the risks outputs for each of the assessment criteria.
Where there in insufficient data provided at the 'Inputs' tab, the 'Results' tab will indicate 'Insufficient Data'. Further input data are required to complete the Level 2 assessment.
Step 6: Determine next steps
The overall risk ranking shown on the 'Results' tab will inform the next steps to be undertaken - see details under 'Level 2' shown above, and flowchart in Figure A (see Assessment Schematic tab).
Appropriate design changes and mitigations are to be applied to the development designs to achieve either 'Very Low' or 'Low' risk ratings.
Step 7: Reporting
Collate the project information as set out in the Odour Technical Standard and submit to SA Water.
Further Information
Background information and details of minimum design rules and appropriate O&C mitigations are provided in the SA Water Odour Technical Standard.

## Assessment Overview (Fig A)
FIGURE A: OVERVIEW OF RISK ASSESSMENT APPROACH

## Definitions
ODOUR AND CORROSION RISK ASSESSMENT TOOL - DEFINITIONS and ABBREVIATIONS
Document Number: | SAW-TS-0854-SUP
Revision Number: | Revision 01
Revision Date: | 2025-09-29
Definitions
High Risk Trade Waste
Trade waste discharges from specific industry types are known to have significant impact on sewage quality thereby resulting in potential higher O&C risks in sewerage networks. These industry types include:
- Dairy processing
- Paper manufacturing
- Food manufacturers and processes
- Drink manufacturers
- Breweries and distilleries
- Meat processors
- Pet food manufacturers
Each of these industries has potential to have levels of BOD, pH, alkalnitiy, sulphate concentration and temperature which are conducive to sulphide generation in sewers, particularly in pressure mains. As a result, they are considered to be 'high risk trade waste' industries and a higher risk rating is applied in the Tool where a new network receives discharges from any of these industry types.
Sensitive Receptors
The definition of sensitive receptors applied in this Tool aligns with the definitions set out by the SA EPA in their current guideline 'Evaluation distances for effective air quality and noise management', issued August 2016 (updated January 2023). Specifically, a sensitive receiver includes any fixed location (including a house, building, other premises or open area) where human health may be affected by air emissions from existing or proposed development, and/or property damage or loss of amenity may be caused by air emissions from the existing or proposed development.
For the purposes of the Tool, the following land uses are considered to be sensitive receptors:
- caravan parks, hotels and motels and tourism accommodation
- childcare centres
- community centres
- consulting rooms
- educational institutions
- hospitals
- nursing homes and retirement villages
- parklands, recreation areas and reserves
- residential dwellings and associated private outdoor recreational areas
Abbreviations
ADWF | Average dry weather flows
ASS | Acid sulphate soils
BOD | Biological oxygen demand
DS | Dissolved sulphide concentration
EPA | Environment Protection Authority
GM | Gravity mains
H2S | Hydrogen sulphide
HRT | Hydraulic retention time
MH | Maintenance holes
O&C | Odour and corrosion
PM | Pressure mains
SPS | Sewage pumping station
SR | Sensitive receptor
SWI | Seawater ingress
TW | Trade waste

## Level 1 Screening
ODOUR AND CORROSION RISK ASSESSMENT TOOL - LEVEL 1 SCREENING CHECKS
Document Number: | SAW-TS-0854-SUP
Revision Number: | Revision 01
Revision Date: | 2025-09-29
Level 1 assessment involves the initial identification of any potential O&C risk triggers. For the proposed sewerage infrastructure development within the physical scope of the assessment, please respond 'Yes' or 'No' to the questions below.
Level 1 Screening Check Questions |  | YES / NO | Data Source
Is there any daisy-chaining of SPS within or upstream of the scope of works? Daisy chaining defined as one or more SPS upstream of the SPS within the scope of work, operating in parallel. |  | YES | To be requested from SA Water.
Is individual asset HRT > 2 hours for any of the PM/SPS, based on ADWF at any stage of development? |  | YES | Designer / Developer
Are there any trade waste discharges from high risk industry types per list provided in 'Definitions' tab, to new sewerage infrastructure? |  | NO | Designer / Developer
Are there any free-fall drops in the proposed development network design greater than 3 metres, along the GM and/or for tributaries entering the GM? |  | NO | Designer / Developer
Are there any existing or potential future sensitive receptors (either within or beyond physical scope of work) within 100 metres of new SPS or vent stacks? |  | NO | Designer / Developer
Are there any deviations to applicable minimum design rules, as set out in the Odour Technical Standard? |  | YES | Designer / Developer
Are there any H2S (g) monitoring data for downstream or upstream assets which indicates elevated risks, e.g. H2S (g) > 10 ppm? |  | NO | To be requested from SA Water.
Are there any known odour hot spots / clusters in existing upstream and/or downstream receiving networks/assets in previous 5 years, attributable to SA Water assets? |  | YES | To be requested from SA Water.
Have there been any known asset deterioration issues (e.g. failures and/or condition assessment assessments indicating rehabilitation/renewal is required) in upstream infrastructure and/or downstream receiving networks as a result of H2S (g) attack? |  | NO | To be requested from SA Water.
Will any of the new assets be constructed of corrodible materials? |  | YES | Designer / Developer
Will the new assets be within 5 km of coastline (potential for seawater ingress)? |  | NO | Designer / Developer
Are there any special sewerage infrastructure assets, e.g. siphons, barometric legs, vacuum sewerage systems, low pressure sewer units, privately owned SPS? |  | NO | Designer / Developer
If YES to any of the above, then proceed to Level 2 assessment. |  | Go to Level 2 Assessment
If NO, document design details and screening tests for submission to SA Water

## Level 2 Inputs
ODOUR AND CORROSION RISK ASSESSMENT TOOL - LEVEL 2 CALCULATOR INPUTS
XX | User input value. Insert 'N/A' where no information is available or is not relevant.
XX | User select from drop down list. Select 'N/A' if no information available.
Item No. | Risk Criteria | Very Low | Low Risk | Medium Risk | High Risk | Units | Inputs | Comments | Guidelines
1 | Pressure main and SPS wet well HRT (hours), at ultimate development | No PMs or SPS | < 2 hours | 2 – 4 hours | >= 4 hours | hours | 2 – 4 hours |  | At ADWF For all new SPS and PM in scope of work. Include all storage facilities (e.g. low pressure sewer assets, storage and overflow tanks and tankering sites). For multiple SPS/PMs, apply calculated aggregate value, i.e. including all SPS/PM assets within scope of work.
2 | Pressure main and SPS wet well HRT (hours), at initial development | No PMs or SPS | < 2 hours | 2 – 4 hours | >= 4 hours | hours | >= 4 hours |  | At ADWF For all new SPS and PM in scope of work, i.e. cumulative. Include all storage facilities (e.g. low pressure sewer assets, storage and overflow tanks and tankering sites). For multiple SPS/PMs, apply calculated aggregate value, i.e. including all SPS/PM assets within scope of work.
3 | Time between pump starts at minimum flow | No SPS | < 1 hour | 1 - 2 hours | > 2 hours | hours | 5 |  | Calculate for each SPS in scope of work and apply highest value. Consider overnight operations.
4 | Number of daisy-chained SPS (upstream of, and within, scope of work) | None | One SPS | Two SPS | Three or more SPS | no. | 1 |  | Includes any known SPS upstream of, and within, scope of work (consider current and potential future). Applies to SPS in series (not parallel).
5 | Flow contribution to downstream assets (at connection point with existing assets) | < 1% | 1 - 10% | 10 – 20% | > 20% | % | 5 |  | Apply highest value calculated using initial and ultimate ADWF.
6 | Trade waste inputs for new development | None | TW discharge types all low risk | Single TW discharge of high risk | Two or more TW discharge of high risk | - | Single TW discharge of high risk |  | Use drop down list to indicate number and risk type for TW discharges in scope of work. See definitions of TW risk types in 'Definitions' tab.
7 | Distance from vent/release point to closest sensitive receptor | No vent / release | > 100 metres | 50 – 100 m | < 50 metres | metres | < 50 metres |  | Applies to any potential sewer gas release point. See 'Instructions' tab for list of applicable sensitive receptor types.
8 | Depth of drops for gravity assets ('free fall' of sewage) | No drops | One drop only and < 3 metres | All drops < 3 metres | One or more drops > 3 metres | - | No drops with free fall distance >= 0.3 metres |  | Includes drops for sewage along primary gravity main route, as well as drops for tributaries entering the primary gravity main route.
9 | Gravity main sewage velocity - maximum (when pipe is flowing full, i.e. at PWWF) | < 2.0 m/s | 2.0 - 2.5 m/s (TBC) | 2.5 – 3.0 m/s | > 3.0 m/s | m/s | 1.5 |  | Calculate for each key sewerage route within scope of work. Apply maximum flow rate for initial and future scenarios.
10 | Gravity main sewage velocity – minimum (at average flow conditions) | > Minimum per Figure X | > 0.9 m/s (TBC) | 0.6 - 0.9 m/s | < 0.6 m/s | m/s | 1 |  | Calculate for each key sewerage route within scope of work. Apply minimum flow rate for initial and future scenarios.
11 | Materials of construction | No corrodible assets | Protective coatings applied to at risk items | Minor equipment items only with corrodible materials | One or more key infrastructure items corrodible, e.g. wet wells, PMs, GMs, MHs | - | Minor equipment items only with corrodible materials |  | For key assets within scope of work.
12 | Pressure main discharge maintenance hole configuration | Submerged entry under all conditions, no risk of splashing | Designed as per SAW standard drawing: Score 1 | Not compliant with SAW standard drawing, but low risk of turbulence | No submerged entry. Entry angle greater than 45 degrees. Elevated risk of turbulence. | - | Low risk of turbulence. Designed with part submerged inlet (per Fig 3-3 in TS 0854) |  | Assesses potential for turbulence for each PM discharge MH within scope of work.
13 | Potential for sulphate ingress to sewer assets via sea water ingress (SWI) OR Potential for sulphate ingress due to leaching via acid sulphate soil (ASS) conditions. | No potential for SWI, > X km from coast | SWI unlikely: Score 1 | Possible (infrastructure located with X km of coast) | SWI is likely. Located within X km of coast. | - | No potential for SWI (> 5 km from coast) AND no risk of ingress of sulphates from acid sulphate soil |  | Based on proximity to coastal areas OR to for areas subject to acid sulphate soils. Applies to assets within and/or upstream of scope or works. Applies where assets are below maximum groundwater table level for some or all of the time.
14 | Potential for sewer gas release (untreated) to atmosphere | No opportunity for gas release | Well sealed MHs Well sealed SPS wet wells | At least one vent on GM with no mitigation and/or One or more ARVs with no mitigation | Several opportunities for sewer gas release to atmosphere | - | Well sealed MHs. Well sealed SPS wet wells. Any releases have effective treatment installed. |  | Assess opportunities for gas release, e.g. from poorly fitted MH covers, vent stacks with no mitigation, air release valves with no mitigation.
15 | Are there special items with potential for increased O&C risks, e.g., barometric loops, siphons, vacuum sewer units, low pressure sewer units, tankering MHs. | No | Yes, but risks are adequately managed | Yes. Some risk management, however not fully effective. | Yes. No effective mitigations. | - | Yes, but risks are adequately managed by use of mitigations (e.g. ventilation and treatment, chemical dosing, non-corrodible materials) |  | Items listed can result in higher risks due to extended HRT, gas pressurisation, introduction of local turbulence, etc. Applies for scope of work and upstream assets.
16 | Where available, estimate of sewage DS concentration at downstream end of scope of works | < 0.2 mg/L | 0.2 - 0.5 mg/L | 0.5 - 3.0 mg/L | > 3.0 mg/L | mg/L | N/A |  | Apply data from monitoring, modelling, calculations and/or estimations based on experience with similar applications (in order of preference).
17 | Where available, estimate of H2S (g) concentration of gas at downstream end of scope of works (90th percentile / peak) | < 5 ppm | 5 - 10 ppm | 10 - 20 ppm | > 20 ppm | ppm | N/A |  | Apply data from monitoring, modelling, calculations and/or estimations based on experience with similar applications (in order of preference).
18 | Expected aggregate upstream HRT for gravity sewers. | < 5 ppm | 5 - 10 ppm | 10 - 20 ppm | > 20 ppm | hrs | 2 |  | Calculated aggregate HRT for gravity systems only, based on ADWF. Estimate of aggregate HRT for upstream gravity network, where applicable, to inform potential for transfer of O&C risks to scope of work (and downstream).
19 | Extent of any known odour and corrosion risks in network upstream of scope of work, e.g. any historical odour complaints (unresolved), measurement data indicating H2S (g) concentrations (90th percentile/ peak) > 10 ppm and/or DS > 0.5 mg/L. | < 5 ppm | 5 - 10 ppm | 10 - 20 ppm | > 20 ppm | - | No indication of upstream O&C risks from data available. |  | Qualitative assessment of extent of O&C risks upstream of scope of work which have potential to impact risks within scope of work (and downstream).

## Level 2 Results
ODOUR AND CORROSION RISK ASSESSMENT TOOL - LEVEL 2 CALCULATOR RESULTS
Item No. | Risk Factor | Units | Inputs | Assigned Risk Level
1 | Pressure main and SPS wet well HRT (hours), at ultimate development | hours | 2 – 4 hours | Medium | Overall Risk Score: | 43.1034
2 | Pressure main and SPS wet well HRT (hours), at initial development | hours | >= 4 hours | High | Overall Risk Level: | Medium Risk
3 | Time between pump starts at minimum flow | hours | 5 | Medium
4 | Number of daisy-chained SPS (upstream of, and within, scope of work) | no. | 1 | Low
5 | Flow contribution to downstream assets (at connection point with existing assets) | % | 5 | Low
6 | Trade waste inputs for new development | - | Single TW discharge of high risk | Medium
7 | Distance from vent/release point to closest sensitive receptor | metres | < 50 metres | High
8 | Depth of drops for gravity assets ('free fall' of sewage) | - | No drops with free fall distance >= 0.3 metres | Very low
9 | Gravity main sewage velocity - maximum (when pipe is flowing full, i.e. at PWWF) | m/s | 1.5 | Very low
10 | Gravity main sewage velocity – minimum (at average flow conditions) | m/s | 1 | Low
11 | Materials of construction | - | Minor equipment items only with corrodible materials | Medium
12 | Pressure main discharge maintenance hole configuration | - | Low risk of turbulence. Designed with part submerged inlet (per Fig 3-3 in TS 0854) | Low
13 | Potential for sulphate ingress to sewer assets via sea water ingress (SWI) OR Potential for sulphate ingress due to leaching via acid sulphate soil (ASS) conditions. | - | No potential for SWI (> 5 km from coast) AND no risk of ingress of sulphates from acid sulphate soil | Very low
14 | Potential for sewer gas release (untreated) to atmosphere | - | Well sealed MHs. Well sealed SPS wet wells. Any releases have effective treatment installed. | Low
15 | Are there special items with potential for increased O&C risks, e.g., barometric loops, siphons, vacuum sewer units, low pressure sewer units, tankering MHs. | - | Yes, but risks are adequately managed by use of mitigations (e.g. ventilation and treatment, chemical dosing, non-corrodible materials) | Low
16 | Where available, estimate of sewage DS concentration at downstream end of scope of works | mg/L | N/A | N/A
17 | Where available, estimate of H2S (g) concentration of gas at downstream end of scope of works (90th percentile / peak) | ppm | N/A | N/A
18 | Expected aggregate upstream HRT for gravity sewers. | hrs | 2 | Low
19 | Extent of any known odour and corrosion risks in network upstream of scope of work, e.g. any historical odour complaints (unresolved), measurement data indicating H2S (g) concentrations (90th percentile/ peak) > 10 ppm and/or DS > 0.5 mg/L. | - | No indication of upstream O&C risks from data available. | Very low

## Calcs and Refs (hidden)
LEVEL 2 RISK ASSESSMENT CALCULATIONS
[6 empty] | Risk Assessment | [7 empty] | Very Low | Low | Medium | High | [6 empty] | Level 1 Screening
Item No. | Risk Factor | Very Low | Low Risk | Medium Risk | High Risk | Adjustment | Input | Units | Risk Score | Adj Risk Score | Adj Risk Level | Max Possible Score | Threshold Reference Data |  |  |  |  | Individual Risk Scores |  |  | Overall Risk Scores |  |  | Responses | YES
|  | Score 0 | Score 1 | Score 2 | Score 3 | [7 empty] | Thresh.1 | Thresh.2 | Thresh.3 | Thresh.4 | Thresh.5 |  |  |  | Min | Max | Risk Assessment |  | NO
1 | Pressure main and SPS wet well HRT (hours), at ultimate development | No PMs or SPS | < 2 hours | 2 – 4 hours | >= 4 hours | yes | 2 – 4 hours | hours | 2 | 3 | Medium | 4 | N/A | No PMs or SPS | < 2 hours | 2 – 4 hours | >= 4 hours | Very low | 0 | Very low | 0 | 20 | Very low risk |  | Unknown
2 | Pressure main and SPS wet well HRT (hours), at initial development | No PMs or SPS | < 2 hours | 2 – 4 hours | >= 4 hours | yes | >= 4 hours | hours | 3 | 4 | High | 4 | N/A | No PMs or SPS | < 2 hours | 2 – 4 hours | >= 4 hours | Low | 1 | Low | 20.0001 | 40 | Low Risk |  | N/A
3 | Time between pump starts at minimum flow | No SPS | < 1 hour | 1 - 2 hours | > 2 hours |  | 5 | hours | 2 | 2 | Medium | 3 | N/A | No SPS | 4 | 6 |  | Medium | 2 | Medium | 40 | 60 | Medium Risk
4 | Number of daisy-chained SPS (upstream of, and within, scope of work) | None | One SPS | Two SPS | Three or more SPS | yes | 1 | no. | 1 | 1 | Low | 4 | N/A | 0 | 1 | 2 |  | High | 3 | High | 60 | 100 | High Risk
5 | Flow contribution to downstream assets (at connection point with existing assets) | < 1% | 1 - 10% | 10 – 20% | > 20% |  | 5 | % | 1 | 1 | Low | 3 | N/A | 1 | 10 | 20 |  | N/A | N/A
6 | Trade waste inputs for new development | None | TW discharge types all low risk | Single TW discharge of high risk | Two or more TW discharge of high risk |  | Single TW discharge of high risk | - | 2 | 2 | Medium | 3 | N/A | None | TW discharge types all low risk | Single TW discharge of high risk | Two or more TW discharges of high risk
7 | Distance from vent/release point to closest sensitive receptor | No vent / release | > 100 metres | 50 – 100 m | < 50 metres | yes | < 50 metres | metres | 3 | 4 | High | 4 | N/A | No vent / release | > 100 metres | 50 – 100 m | < 50 metres
8 | Depth of drops for gravity assets ('free fall' of sewage) | No drops | One drop only and < 3 metres | All drops < 3 metres | One or more drops > 3 metres |  | No drops with free fall distance >= 0.3 metres | - | 0 | 0 | Very low | 3 | N/A | No drops with free fall distance >= 0.3 metres | One or more drops, at least one with free fall > 0.3 and <= 0.5 metres | One or more drops, at least one with free fall > 0.5 and <= 3.0 metres | One or more drops, at least one with free fall > 3.0 metres
9 | Gravity main sewage velocity - maximum (when pipe is flowing full, i.e. at PWWF) | < 2.0 m/s | 2.0 - 2.5 m/s (TBC) | 2.5 – 3.0 m/s | > 3.0 m/s |  | 1.5 | m/s | 0 | 0 | Very low | 3 | N/A | 2 | 2.5 | 3
10 | Gravity main sewage velocity – minimum (at average flow conditions) | > Minimum per Figure 8-2 of TG0530 (TBC) | > 0.9 m/s (TBC) | 0.6 - 0.9 m/s | < 0.6 m/s |  | 1 | m/s | 1 | 1 | Low | 3 | N/A | 1.2 | 0.9 | 0.6
11 | Materials of construction | No corrodible assets | Protective coatings applied to at risk items | Minor equipment items only with corrodible materials | One or more key infrastructure items corrodible, e.g. wet wells, PMs, GMs, MHs | yes | Minor equipment items only with corrodible materials | - | 2 | 3 | Medium | 4 | N/A | No corrodible assets | Protective coatings applied to at risk items | Minor equipment items only with corrodible materials | One or more key infrastructure items corrodible, e.g. wet wells, PMs, GMs, MHs
12 | Pressure main discharge maintenance hole configuration | Submerged entry under all conditions, no risk of splashing | Designed as per SAW standard drawing: Score 1 | Not compliant with SAW standard drawing, but low risk of turbulence | No submerged entry. Entry angle greater than 45 degrees. Elevated risk of turbulence. | yes | Low risk of turbulence. Designed with part submerged inlet (per Fig 3-3 in TS 0854) | - | 1 | 1 | Low | 4 | N/A | Submerged entry under all conditions, no risk of splashing and no/low turbulence. | Low risk of turbulence. Designed with part submerged inlet (per Fig 3-3 in TS 0854) | Compliant with SAW standard drawing 4005-20008-01 | No submerged entry, OR entry angle greater than 45 degrees, OR elevated risk of turbulence.
13 | Potential for sulphate ingress to sewer assets via sea water ingress (SWI) OR Potential for sulphate ingress due to leaching via acid sulphate soil (ASS) conditions. | No potential for SWI, > 5 km from coast | SWI unlikely and/or no infiltration via assets confirmed | Possible. Infrastructure located with 2 km of coast. | SWI is likely. Assets located adjacent coastline and no/minimal mitigation. |  | No potential for SWI (> 5 km from coast) AND no risk of ingress of sulphates from acid sulphate soil | - | 0 | 0 | Very low | 3 | N/A | No potential for SWI (> 5 km from coast) AND no risk of ingress of sulphates from acid sulphate soil | Sulphate ingress, via SWI or ASS, unlikely and/or no infiltration via assets confirmed | Possible sulphate ingress via SWI (infrastructure located with 2 km of coast), or via ASS. | Sulphate ingress is likely. Assets located adjacent coastline, OR assets located in an area of ASS. No/minimal mitigation.
14 | Potential for sewer gas release (untreated) to atmosphere | No opportunity for gas release | Well sealed MHs Well sealed SPS wet wells | At least one vent on GM with no mitigation and/or One or more ARVs with no mitigation | Several opportunities for sewer gas release to atmosphere | yes | Well sealed MHs. Well sealed SPS wet wells. Any releases have effective treatment installed. | - | 1 | 1 | Low | 4 | N/A | No opportunity for gas release | Well sealed MHs. Well sealed SPS wet wells. Any releases have effective treatment installed. | At least one vent with no mitigation and/or an asset known to be poorly sealed. | Several opportunities for sewer gas release to atmosphere.
15 | Are there special items with potential for increased O&C risks, e.g., barometric loops, siphons, vacuum sewer units, low pressure sewer units, tankering MHs. | No | Yes, but risks are adequately managed | Yes. Some risk management, however not fully effective. | Yes. No effective mitigations. |  | Yes, but risks are adequately managed by use of mitigations (e.g. ventilation and treatment, chemical dosing, non-corrodible materials) |  | 1 | 1 | Low | 3 | N/A | No | Yes, but risks are adequately managed by use of mitigations (e.g. ventilation and treatment, chemical dosing, non-corrodible materials) | Yes. Some risk management, however not fully effective. | Yes. No effective mitigations.
16 | Where available, estimate of sewage DS concentration at downstream end of scope of works | < 0.2 mg/L | 0.2 - 0.5 mg/L | 0.5 - 3.0 mg/L | > 3.0 mg/L |  | N/A | mg/L | N/A | N/A | N/A | 0 | N/A | 0.2 | 0.5 | 3
17 | Where available, estimate of H2S (g) concentration of gas at downstream end of scope of works (90th percentile / peak) | < 5 ppm | 5 - 10 ppm | 10 - 20 ppm | > 20 ppm |  | N/A | ppm | N/A | N/A | N/A | 0 | N/A | 5 | 10 | 20
18 | Expected aggregate upstream HRT for gravity sewers. | < 2 hours | 2 - 4 hours | 4 - 6 hours | > 6 hours |  | 2 | hours | 1 | 1 | Low | 3 | N/A | 2 | 4 | 6
19 | Extent of any known odour and corrosion risks in network upstream of scope of work, e.g. any historical odour complaints (unresolved), measurement data indicating H2S (g) concentrations (90th percentile/ peak) > 10 ppm and/or DS > 0.5 mg/L. | No indication of upstream O&C risks from data available | Some known minor issues only, e.g. single odour complaint. | Moderate indications of O&C risks, e.g. H2S (g) monitoring indicates > 10 ppm, more than one odour complaint. | Data indicates potential significant risk, e.g. several odour complaints, asset failure reports. |  | No indication of upstream O&C risks from data available. | - | 0 | 0 | Very low | 3 | N/A | No indication of upstream O&C risks from data available. | Some known minor issues only, e.g. single odour complaint. | Moderate indications of O&C risks, e.g. H2S (g) monitoring indicates > 10 ppm, more than one odour complaint. | Data indicates potential significant risk, e.g. several odour complaints, asset failure reports.
[6 empty] | TOTAL RISK SCORE |  |  | 21 | 25 | Medium Risk
[6 empty] | Total max possible score |  |  |  | 58 |  | 64
[6 empty] | Risk % |  |  |  | 43.1034

## Risk Caterogies (hidden)
LEVEL 2 RISK ASSESSMENT CATERGORIES
Categories for risk visual indicator |  |  |  | Level 2 results for visual indicator:
Performance Label | Category Value | Labels | Values | Labels | Values
Very Low Risk | 20 | 10 | 10 | Pointer | 43.1034
Low Risk | 19.9999 | 20 | 10 | Thickness | 1
Medium Risk | 20 | 30 | 10 | Rest | 155.8963
High Risk | 40 | 40 | 10
Total | 99.9999 | 50 | 10
|  | Total | 50
43